[image: image1.jpg]



[image: image2.jpg]member of The Eﬂ}lﬁ Group™




[image: image5.wmf]3767 Alpha Way

Bellingham WA 98226

United States

Tel: 360 647 2360

Fax: 360 671 4936

www.alpha.com

                                                                                                                       


[image: image3.wmf]

Alpha Technologies, Inc. - Bellingham



April 29, 2014
Troutdale Questions:

EXTERIOR SOW:
 

Architectural 7: We assume that other equivalent structural systems to tilt-up concrete would be acceptable.
Tilt up is preferred to match the existing structure. CMU can be an alternative if the exterior matches. 
(RHW) The 2013 scheme was for CMU walls (8” or 10” per structural engineer) with an exterior screen wall system including the necessary code insulation. There could be opaque glass storefront windows and doors included to match the 2002 design without having to make the overall wall thicker and painted CMU would be interior wall finish. The exterior wall finish would be an acrylic plaster with reveals to emulate the existing concrete tilt-up panel rustication strips. This avoids having a large crane on the slab and allows wall construction to start as soon as the 2002 footings are exposed.  Drawbacks are that this type of rain screen system is relatively new and that the plaster reveals won’t exactly match the tilt-up panel rustication strips.
Architectural 12: The two-hour roof/ceiling rating was clarified at one time as from the exterior side only. Is that clarification still true?
Yes per our insurance carrier 2 hour rating is adequate.

(RHW) 2-hour from the outside only.
I didn’t see anything for seismically upgrading the existing building in either scenario. They did talk about this at pre-bid walk-throughs.

I didn’t see anything for seismically upgrading the existing floor for the Exterior scenario.
The existing slab will need to meet the current seismic rating for the area. 

(RHW): Adam, please comment. It doesn’t sound like a big deal.
(AJS) We will add to our scope for the raised floor. I am assuming for both the interior and exterior expansion that the intent is to update the existing shell to be upgraded to the requirements for Chapter 16 for essential facility. 

AC Electrical SOW:

Utility service is called out as 1600A, service to the building as 1200A, 1600A transfer switches, 1200A (1000 KW at PF=1) generators, 1600A main breaker in generator. Is this correct? 1600 amp not 1200 amp. 
(RHW) Will the generators need to be larger, 1250KW?
Generator SOW:

Please provide the Comcast Standard containing the Arcadis permitting information for generators.

Is there two load banks or one?  I think you need two or controls might get overly complicated. Two load bank connections. We cannot do an either/ or on the gens. Each must be treated indivisually.
(RHW): I didn’t see how you could do the either/or option either.  The problem is where to put these load banks where they can dissipate their heat and not melt nearby objects. Are we worried about winter time ice in Troutdale causing an issue for these units? It seems odd to add heat tape to a giant toaster.
Electronic fuel gauging, fuel alarms and interstitial leak alarms to XOC where required for the Interior SOW but not for the Exterior SOW, is this correct? Sorry should have been on the exterior SOW as well. Please include. 
 

Security SOW:

Please provide the latest Comcast Standards which this is supposed to be design to meet. As I recall this was an older system and we budgeted for replacement of the perimeter security and door access systems and the addition of video monitoring. There is very little time to make these judgments and price this so we need some way to quantify these systems so we can price them. 
I’ve attached the latest standard. All new build must accommodate the standard. 

(RHW) I didn’t see the standard attached.
Infrastructure SOW – Please provide more information for this Q&A statement. Please note that there are 20 four inch conduits stubbed toward the addition (10 from existing Headend, 6 east & 4 west).

Where are the fiber vaults which need upsizing? Vaults: First vault front of building close to flag pole, Second is in back yard N/E corner next to dish #16 PS.
(RHW) These could be custom additions using prefabricated lids (if possible) from Oldcastle or somebody like that. Mackenzie would need some structural time for this.  The vault in the N/E corner of the backyard is in a very difficult place near the corner and next to a satellite antenna foundation so getting a crane back there will be interesting. For the front vault we’ll just need to be careful around the flag pole’s in-ground sleeve and to repair the landscaping and irrigation at the front. The depth at 8’ can be a problem and any time you dig in Troutdale you can run into automobile size Missoula Flood stones. Please explain better the 16 conduits. Is that 16 from each side or is 16 total? As I recall there was very little room to get the conduits installed in 2002 around the east end of the building and they were shallow and concrete encased so good luck with that one. Should the unused vault on the west side of the addition installed in 2002 be removed and the conduits patch through.  This simple note is a big deal, easily 6 figures+ especially working around their existing fiber with excavation equipment and concrete saws.
 There is one empty vault installed on the west side of the addition.
Where any cable slots required to get DC cable to the new addition? Yes two, 24” wide x 12” tall PS
(RHW) Adam please comment, I assume we won’t need wall reinforcement if we can stay away from tilt panel edges.

(AJS) We will need some form of minimal reinforcing (it would not require floor to ceiling HSS). 
“Does there need to be conduit connections or cable slot between the Building Addition and new Head-End to facilitate the cut-over? Yes two openings, 10” x 6”, fire-stopped ready PS
Two locations, upsize fiber vaults (7’ x12’ X 8’ tall), Sixteen 4” schedule 40 conduits. Diverse vaults/paths stub up main hub floor east west walls.”

 

INTERIOR SOW:
 

Architectural 6d: “Is there to be a rated drywall ceiling installed?”  A question was provided here and no state of work was made, please clarify.  This would also apply to the old Control Room area and to the Electrical Room which may need a 2nd layer of drywall to align with the ceiling in the Storage area. Since the drywall support at the Electrical Room is unknown the plane of the ceiling may not be the same as the surrounding area and it may need to be removed and framed similarly to the Storage area then two new layers of 5/8” Type-X drywall applied. Please note that adding a drywall ceiling in the existing Headend will require a temporary dust-proof work platform, removal of all the economizer system ductwork, patching holes in the exterior wall where the ductwork was removed, framing between the metal trusses, furring on the metal framing and application of two layers of drywall, finished taping, painting and relocation of lighting fixtures and other electrical and fire alarm devices. Because the roof slopes to scupper drains on the south side of the building some of the work may require temporary devices like auto mechanic creeper dollies because the clearances may be limited.

  Yes there needs to be a 2 hr rated ceiling  ( dry wall) to be installs once the tiles are removed. It is understood that dust and debris will need to be mitigated during the build out. 
(RHW) We will match the 2002 detail which is metal stud stick framing on top of the steel OWJ bottom flange, hat channel furring to get the drywall below the bottom plane of the OWJs and then two layers of 5/8” Type-X drywall with Level 4 (smooth) finish.  This is nominally 2-hour rated from room side (90 minutes or so).
Architectural 12: Should 4 satellite dishes be removed in lieu of 3. Yes four dishes # 09,10, 13,14 PS
 

Architectural: The Exterior SOW has a statement of providing insulation per the Oregon Energy Efficiency Specialty Code but the Interior SOW has no equivalent statement. If this is required for the Interior SOW there will be lots of potential issues with a structure designed in the early 1990’s lacking perimeter code insulation systems and with walls covered with electrical and mechanical systems which are by most parts essential systems.
If we are not touching the exterior walls on the interior build out then no further insulation would should be required (unless the city stipulates). For the new exterior, it has to meet current code.
(RHW) So we will ignore the insulation on the Interior SOW and Alpha will stipulate that the City will take the risk.  Since no HVAC load calcs appear to have been completed it doesn’t appear like we need to ask about that at this time,
In the interior scope, what is the purpose of the 600 SF storage building located on the existing slab. This is for storage on the interior SOW only. Yes it will be conditioned and lighted. 
o   Is it conditioned space

o   Will it have lights.
-          The exterior scope indicates  9,525 SF for the expansion. Is more like 7,500 with 2,000 SF of an enclosed yard for HVAC on the ground. Has this been clarified? The one concern is if we do not build to the perimeter of the slab, we will need to cut and pour new footings for the 7500sq ft building. Since we are placing the HVAC on the pad, I would call it out for 7500sq ft. 
 (RHW) Adam please review. I assume where an exterior wall is introduced near Grid Line B that we will still need a new wall footing butted to the column footings.
(AJS) Yes, this area will need a new wall footing.
AC Electrical SOW:

Utility service is called out as 1600A, service to the building as 1200A, 1600A transfer switches, 1200A (1000 KW at PF=1) generators, 1600A main breaker in generator. Is this correct? Same as above. 1600A end to end. 
 

 

Interior/Exterior Ground Upgrades SOW

Bond MGB to building steel.  I assume this means exposing rebar in an existing concrete assembly? As long as the rebar is bonded to all other building metal. 
 

HVAC Upgrade SOW:

The requirement is for installed exterior…split systems unit. Since Exterior packaged units were discussed at the walk-through this statement needs clarification.  Additionally we recorded finish ceiling heights at the site and looked at the roof/ceiling slopes and have roughed out a sketch of how they may appear and compared that to a 11’-6” AFF minimum bottom of duct and the vertical space for ductwork appears to vary from a minimum of 12” to a maximum of 27”.  There will be other limitations for penetration the wall with new ductwork such as conduits in and out of panels in the Electrical Room and Headend and supply ductwork coming off the top of Liebert units in the Headend. Taking all limitations into account and recognizing you need to get supply and return air out the same wall this borders on impossible without lots of pre engineering which no there is no time provided for in this RFQ.  If split systems are desired no footprint for the units and associated clearances has been allow.  Two units in the expansion area of the Headend along with the electrical service elements which remain raise the possibility that there will be significant loss of rack space.
Yes package units would most likely be the best path. It was my oversight that was missed. We can allow more time for engineering of the HVAC. You just need to ask. I would extend that to all companies that the RFQ went out to. 

(RHW) Nate, how much time do you need to pre-engineer something that may not be possible to build without raising the roof?  Chaun how much time are they giving us?
Additionally a fully ducted return and hot/aisle-cold/aisle does not seem feasible because of the lower ceiling height and the inability to get two sets of ductwork by each other except at the perimeter wall.

 

Security SOW:

Please provide the latest Comcast Standards which this is supposed to be design to meet. As I recall this was an older system and we budgeted for replacement of the perimeter security and door access systems and the addition of video monitoring. There is very little time to make these judgments and price this so we need some way to quantify these systems so we can price them. Outlined in the standard. 
DC Power:

With strapping the plants to a main 10kA bus, are we removing the internal horizantal bus of the existing DC Plants? Yes if needed for space.
You are calling out making provisions for 44 fuse positions…  does that include whats already there or what you want with the new supllemental bay. New supplemental bay
Do you really want 2 more battery strings?  You should have more than enough with the current battery configuration. Please make provisions for additional strings for future growth. Not needed for day 1 build.
[image: image2.jpg]

[image: image4.wmf]Alpha Technologies, Inc.

[image: image5.wmf]