## Sheet1
Comcast Troutdale |  |  |  | 2014-04-22
Clarifications
| 1. | Clarification is needed as to the location of the new transformer.
There is a large vault and conduit system installed beteen the two front parking spaces
and the front of the building. See the 2002 drawings (if they gave us that sheet, otherwise let me know).
| 2. | Clarification is needed as to the location of the new Electric Room relative to the
existing Transformer.
There are secondary conduits installed in 2002 which run from the transformer vault to the storge
Review the 2002 drawings for count and approximate location. (1-4" primary, 8-4"secondary)
| 3. | In reference to Architectural SOW item 12, we are assuming that the removal of the
dish electrical is budgeted by others.
|  | Remove antenna & dispose |  |  | ?
|  | Remove foundations and fill holes |  |  | RHW
|  | Trenching for conduits, grounding & gas piping |  |  | RHW
|  | Remove satellite coax |  |  | ?
|  | Remove power to dish heaters |  |  | ?
|  | Cut back grounding |  |  | ?
|  | Cap/remove gas piping |  |  | RHW
|  | Rework conduits to four dishes to the east |  |  | ?
|  | Pull back and reinstall conduits to the four dishes on the east |  |  | ?
|  | Maintain grounding continuity of UG wire to four dishes on east |  |  | ?
|  | Rework gas piping for for dishes on east (Not required, feed north to south |  |  | RHW-NR
| 4. | In reference to Architectural SOW item 13, we are assuming that the repair or
replacement of the Gate Controls is budgeted by others.
I'm note sure they will be damaged but Alpha may want to carry an allowance
| 5. | In comparing AC Electrical SOW item 1 to item 4, we assume that we are supplying a
1600 amp service.
Generator size vs. breaker is interesting also.
| 6. | In reference to AC Electrical SOW item 5, we are assuming that the transformers are
existing and are to be refed.
On the interior remodel there are two which may need to be relocated. Alpha should comment.
| 7. | In reference to AC Electrical SOW item 6, have critical loads been identified.
| 8. | In reference to AC Electrical SOW item 8, should the panel to be refed be Panel MDP
or DP-1, not EP-1?
Feeding the MDP is probably not helpful except the feeder to Panel A would need a new home.
Feeding ESB would use less space if it's legal to do so, Panel A can be picked up and there is enough capacity.
| 9. | In reference to AC Electrical SOW item 9, the following has been identified as being
relocated, please confirm.
Feeder to Panel A1 located on Control Room Wall
Feeder to Panel B1 located on Control Room Wall
Feeder to 45 Kva Transformer feeding AMP80 above ceiling of Control Room
AMPS80 45 Kva Transformer and Disconnect
Feeder to 75 Kva Transformer feeding AMP80 above ceiling of Control Room
AMPS80 75 Kva Transformer and Disconnect
Feeder to Panel UPS-1
Panel UPS 1
Feeder to UPS 2
Reference Ground from MGB
| 10. | Approximate locations are needed as to where the following are to be located.
AMPS80 45 Kva Transformer
AMPS80 75 Kva Transformer
Panel UPS 1
New Panel A2
New Panel B2
| 11. | In reference to AC Electrical SOW item 9, the following has been identified as being
removed from service, please confirm.
Existing Utility Service Entrance conductors
Generator & Generator System wiring
Generator Fuel system wiring
Existing HVAC Units on South side of Building
Control Room wiring
The old MDP upstream of the ATS is using lots of space.
| 12. | In reference to Generator Installation, please confirm the following:
Gen to Gen ATS & Util to Gen ATS are to be located in New Electric Room
Gen to Roll-up Gen MTS with lug box is to be located near the generators
Two load banks?
| 13. | In reference to DC Power Upgrade SOW item 2, Is the bus duct to continue into the
Headend area?
| 14. | In reference to DC Power Upgrade SOW item 2b, is quantity of 12) Battery Shunts
correct and are they to be integrated into the Bus duct system?
| 15. | In reference to DC Power Upgrade SOW item 2d,e,f, are fused positions to be installed
as part of the Bus duct system or as part of the Distribution Bay?
| 16. | In reference to DC Power Upgrade SOW item 7, 8,9 clarification of locations and cabling
requirements.
| 17. | In reference to DC Power Upgrade SOW item 10, clarify which diverse circuits are
referenced.